## Background
AMI Solution
National Fuel
July 2023
Background: An AGA member company is in the process of investigating the feasibility of moving forward with an Advanced Metering Infrastructure (AMI) initiative. As part of this review, this AGA member is interested in learning about other AGA members’ experience with an AMI solution.
Note: The survey responses are based on an informal survey and are for general information only. They are not intended to bind any company or state a company's official position. The information represents an unaudited compilation of information and could contain coding or processing errors. Anyone using this document should rely on his or her own independent judgment or, as appropriate, seek the advice of a competent professional. References to work practices, products or vendors do not imply an opinion or endorsement by AGA or a responding company. This publication is confidential and proprietary to AGA. This document is not intended to provide legal advice or opinions. As always, you should consult your legal counsel for advice based on the law and your company’s specific facts and circumstances.
Copyright & Distribution: Copyright © 2023 American Gas Association. All rights reserved. This work may not be reproduced or transmitted in any form or by any means, electronic or mechanical, including photocopying, recording, or by information storage and retrieval system without permission in writing from the American Gas Association.

## Summary Of Responses
Responding Company: | Does your utility currently utilize AMI technology for gas metering? | When did you implement this technology? | What percentage of current gas customers and how many meters are read using AMI technology? | What communications technologies are being utilized for gas AMI? | If using gas AMI technology, do you obtain onsite visual verification of meter reads and if so, how often | If using gas AMI technology, what other functionality, if any, do you utilize AMI besides collecting gas metering information? | If you’ve implemented AMI, what is your software solution and who was your solution integrator for both residential and commercial/industrial? Note: Please only provide the name of the software used and the name of the solution integrator. Do not provide any endorsement or assessment, either positive or negative, of any specific product, vendor, or service provider. | If your company has implemented AMI technology, has it changed how your company applies rates/billing? | If your company has implemented AMI, have you encountered any operational issues with the devices? If YES, please explain. | If your company has implemented AMI, does your company only install on meters that are outside? | If also installed inside, has your company developed a process for replacing the AMI devices? If YES, please explain. | Do you wish your responses to remain anonymous when a survey summary is posted on the members-only side of the AGA website? Please type YES or NO.
Washington Gas | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | NO
Orange & Rockland Utilities | Yes | July 2017 - October 2020 | 99.7% of Gas customers are read using AMI technology. 142,097 meters have AMI gas devices installed. | ITRON/Silver Springs Network Gas IMU devices are being used. | We do not obtain on site visual verification of meter reads on a scheduled basis. When troubleshooting gas AMI devices, the meter technician always records a manual read. | Volume Correctors, Gas Interruptible Programs, Methane Sensors | ITRON/Silver Springs Network - AMI System Integrator - IBM | No | We have encountered operational issues with the IMU device installed on many of our gas meters. There is a magnet in the IMU that comes loose at times which causes communication problems. Installation of these IMU devices can be difficult as well. The set up of the oruginal IMU from SSN has the battery positioned on the right of the device. This caused some issues where the IMU did not fit in the current metering set up. Itron has developed a device that is front facing which has solved some of the spacing issues for installation. | We installed AMI devices on all meters regardless of location. | We used a meter installation vendor to complete this part. They were tasked with making 5 attempts during various times throughout the day/evening/Saturdays. We also developed a robust communication plan to let our customers know when we were coming to their home to complete the install. | NO
Entergy | Yes | 2.5 years | About 98.08% of our customers. We currently have approximately 205,000 out of 209,000 customers being read using AMI technology. | AMI uses Itron 500G models and Communications are carried out through the Gen 5 Mesh network. | Entergy Gas only obtains onsite visual verification of meter reads on a “when needed” basis. There is no planned schedule or route determining when on site visual verifications take place. | Entergy Gas currently only uses AMI technology for meter reads. | 8. Entergy Gas only uses AMI for residential/commercial customers or more specifically, customers that don’t require real time pressure/temp correction. Software solution and integration was third party done by IBM. SAP customer care systems makes CPS. Entergy IPE was done by Siemens. All the readings come through utility IQ. |  | The operational issues we’ve encountered are communication failures, firmware failures and most commonly IMU failures. We also have data integrity issues with meter/IMU mismatches in the billing system. | Entergy Gas installs AMI technology on both outside and inside meters. | Entergy Gas only replaces AMI devices when needed. There is no planned process or planned schedule for device replacement. Not yet, but there will be because of the batteries. They have a 20 year life. | NO
Colorado Springs Utilities | Yes, currently deploying ~220k AMI gas endpoints | AMI deployment started in 2021. Expected completion in 2024. | AMR 50%, AMI 50%, ~220k endpoints total | RF (902-928 MHz) | Yes, conducting QA/QC on intial install and follow-up read verification sample. Recently completed read drift verification on AMI modules installed in 2021. | AMI for electric meters and water modules | Landis+Gyr Command Center, Texas Meter & Device (TMD) | Not currently but could support TOU rates in the future. | No major operational issues yet. | Yes, per our standards. A very small percentage of meters could be considered "inside" but are still open to atmosphere. | No, our AMI gas technology connects to the nearest AMI electric meter so we don't have connectivity issues. We do have an interior metering standard for our AMI electric meters. | NO
Nicor Gas | Yes | Between 2018 and 2022. | Over 99% of customers/meters are being read using AMI technology. ~2.2M AMI devices are currently deployment. | A point-to-multipoint solution was implemented at Nicor Gas. | Read validation was done on initial install for all premises, prior to certifying the customer location. On-going, any field visit that captures a read has that read checked for accuracy. | During the winter months, the private AMI network is also leveraged for some pressure monitoring equipment. | Sensus' AMI technology and software was utilized. | No | No | Devices have been installed on both inside and outside meter locations. | Standard processes (i.e. contacting customers, making appointments) for inside locations apply to any AMI device maintenance that is needed. | NO
South Jersey Gas | We are in the process of implementing AMI within our service territory. | We plan to roll out AMI technology within the next 2 years. | N/A - SJG is in the process of implementing this technology and plans to add them to all our gas customers (+400,000). | SJG plans to use cellular connection to collect reads. | N/A | We don't plan to use additional functionality at this time. | The solution that we plan to implement is a SaaS solution. | N/A - SJG is in the process of implementing this technology. | N/A - SJG is in the process of implementing this technology and we have not come across major operational issues with the devices during initial installations. | We plan to install AMI on both inside and outside meter sets. | N/A - We have not developed a process yet. | NO
Dominion Energy Ohio | No. We currently have a business case underway to look at AMI technology and smart meters. | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | NO
NiSource | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | NO
NW Natural Gas | Not Currently | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | NO
UGI Utilities | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | NO
ConEdison Co. of NY | Yes | 2017 | ~98% (1.1 million) | Mesh network utilizing RF from access points to meter & meter to meter. Cellular from access points to back-office data collection systems. | Only for Opt-out customers, legacy meters pending up-grades to AMI, or AMI meters which are not on the network. Read bi-monthly. | Natural gas detectors (in-production) and Over capacity alarms (in-development). | Software solutions and integrators have been the same for residential, commercial and industrial. The IT end of AMI is a mix of applications. Would need to refer to an AMI-IT specialist for specifics. | Unsure. | Yes. AMI devices on meters with electronic correctors provide serial data which adds complexity with regard to keeping the | No. AMI is applied to meters inside and out. | Currently, AMI devices are replaced if the unit is failing to communicate, if reads fail to advance, or if the battery is dead. | NO
Southern California Gas Co. | Yes. | First advanced meter was installed in 2012. | As of July, 2023, we have 6.1M meters on the AMI system. Only 8,500 customers have opted out of the AMI technology and are being manually meter read, bi-monthly. | SoCalGas uses the XXXX AMI system which is a private radio network operating in the 450MHz space. | As identified above we manually meter read approx 8,500 accounts due to opt out. We also have multiple work order types that require a technician to obtain a meter read as part of the work order. This data is used to validate AMI read/equip. validation. | We have approximately 2,000 Pressure Monitors on our network, transmitting hourly pressure reads (Honeywell EC350s and Mercury units). In addition, next month, we will be deploying 500 residential methane detectors (New Cosmos). In both cases, once an alarm threshold is exceeded, the units will transmit their reads minutely. We also utilize the consumption activity at each location to run through Machine Learning models to identify operating anomalies. These outputs are used for safety, diversion identification, system capacity forecasting, energy efficiency.. | SoCalGas uses the entire XXXX software suite. The system integrator for the original installation was XXXXX. | No. | All technology requires maintenance, and AMI system is no different. More specific information is available upon request. | No. 5.5 million meters are outside. The remaining 500,000 meters are in confined space locations such as basements, garages, cabinets, etc. | AMI devices are installed on the meter wherever the meter resides, either indoor or outside. For indoor meters, we use a variety of solutions such as extended range Meter Transmission Unit’s (MTU), remote mount MTU’s and indoor Data Collector Units for large, underground parking structures. | NO
COMPANY 1 | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | YES
COMPANY 2 | Yes | 2008 | 51% of gas customers meters are read using AMI technology – 679,908 currently read using that technology. | 2.4 GZ | We obtain onsite visual verification of meter reads when investigating the site for various reasons (meter assembly checks, meter inspections, meter changes, module changes, etc.) on an as needed basis | None | Itron | No – it has just changed the way we are able to pull reads to bill customers. | Yes – sometimes the wake-up process for the device does not happen upon installation which causes issues with getting reads back to the billing system. Also – in some cases, AMI does not work because the signal can’t get to an electric meter due to the location of the gas meter (i.e. in basement, surrounded by concrete, etc.) | No – inside meters also get AMI’s installed on them. | We have a program in which we are working to move all meters outside, they may be replaced during that process or when there is a need to pull the meter based on testing requirements with our regulatory body. Additionally, if the devices have low batteries, we will also replace them. | YES
COMPANY 3 | Yes | 2012 | 100% - 567,546 meters | Point to Point communications using RF Sensus Flexnet protocol. | Yes, pending no read meters need verified usage updates periodically. | None at the moment | Sensus RNI Head End Network | It has allowed us to bill more accurately estimated bills and implement Time of Use solutions to customers. | No. | No, we install indoor and outdoor meters. | Yes, we use the Customer Appointment Process to schedule appointments with customers that have indoor meter locations. | YES
COMPANY 4 | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | YES
COMPANY 5 | No | N/A | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | YES
COMPANY 6 | No | N/A | 0% | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | YES
COMPANY 7 | Yes | 2018 | Less than 2% | Landis and Gyr Gridstream Network | Yes, every 6 months | None | Command Center | No | Yes, the devices will sometime stop working and need to be replaced | No | No | YES
COMPANY 8 | Yes | AMI 2018 | 93% complete of ~800,000 gas population | RF Mesh | During the exchange yes and if there is a network issue or read interruption, a manual read is deployed. | AMI electric and smart streetlights | Landis+Gyr, RF Mesh Gridstream | No, we had AMR technology before. | Continue to observe any patterns while transitioning from AMR to AMI. | Inside meter rooms and outside on structures. | Implemented a Meter Upgrade conversion project that is strategically addressing the service territory in coordination with customers. | YES
COMPANY 9 | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | YES
COMPANY 10 | Yes | In the last 5 years. | We have approx 600k customers on a gas AMI solution, that is approx 70%. | Itron Fixed Network | These are done through service calls and through our testing program. | NA | We are using the Itron software (collection manager, FND | Yes | Yes, there can be issues with the devices communication to the mesh and issues with the mesh collapsing and reforming. | No | No, they are maintained as needed. When originally replaced customers were notified. A lot of effort was put into communicating with and working with customers. | YES
GAS Summary: AMI Solution
July 2023
AGA Contact: Luis Escobar
Note: The survey responses are based on an informal survey and are for general information only. They are not intended to bind any company or state a company's official position. The information represents an unaudited compilation of information and could contain coding or processing errors. Anyone using this document should rely on his or her own independent judgment or, as appropriate, seek the advice of a competent professional. References to work practices, products or vendors do not imply an opinion or endorsement by AGA or a responding company. This publication is confidential and proprietary to AGA. This document is not intended to provide legal advice or opinions. As always, you should consult your legal counsel for advice based on the law and your company’s specific facts and circumstances. The information provide in this summary is for the benefit and internal use of individual AGA members. It should not be discussed among the participants or members nor provided to others.
Copyright & Distribution: Copyright © 2023 American Gas Association. All rights reserved. This work may not be reproduced or transmitted in any form or by any means, electronic or mechanical, including photocopying, recording, or by information storage and retrieval system without permission in writing from the American Gas Association.