## Background
Meter Set Assembly
Sourthern Company
August 2023
Background: Meter Set Assembly (“MSA”) pressure testing is a stage in manufacturing where the manufacturer verifies all mechanical/threaded joints are completely sealed. An AGA member company, Southern Company Gas, is evaluating the pros and cons of utilizing different standardized codes for pressure testing MSAs to help pre-emptively catch leaks before the installation of the MSA. As part of this evaluation, this AGA member is interested in other AGA members’ practices and experiences in this area.
Note: The survey responses are based on an informal survey and are for general information only. They are not intended to bind any company or state a company's official position. The information represents an unaudited compilation of information and could contain coding or processing errors. Anyone using this document should rely on his or her own independent judgment or, as appropriate, seek the advice of a competent professional. References to work practices, products or vendors do not imply an opinion or endorsement by AGA or a responding company. This publication is confidential and proprietary to AGA. This document is not intended to provide legal advice or opinions. As always, you should consult your legal counsel for advice based on the law and your company’s specific facts and circumstances.
Copyright & Distribution: Copyright © 2023 American Gas Association. All rights reserved. This work may not be reproduced or transmitted in any form or by any means, electronic or mechanical, including photocopying, recording, or by information storage and retrieval system without permission in writing from the American Gas Association.

## Summary Of Responses
Responding Company: | Based on your company’s existing policies and practices, to what current specification(s) does your company require manufacturers to pressure test your Meter Set Assemblies (MSAs)? | Other (please specify) | Have manufacturing specifications related to leak testing your products changed in the past 10 years? If so, please specify how they have changed. | Is your company currently exploring any new manufacturing standards for MSAs related to emissions abatement? | Have there been any issues with the acceptance of electronic pressure testing boards versus traditional leak testing (i.e., “dunk-test”) for MSAs used by your company? | Do you wish your responses to remain anonymous when a survey summary is posted on the members-only side of the AGA website? Please type YES or NO.
Dominion Energy Ohio | Other (please specify) | Per ASME B31.3, and DOT 192.501 | No changes | We began full NDT on all welded assemblies in 2020, but not due to "emissions abatement". Under 100 psig, 2" and smaller, are not in scope. | One fabricator still dunk tests, most others use electronic pressure recorders, with no issues. | NO
UGI Utilities | ASTM E515 – Standard Practice for Leaks Using Bubble Emission Techniques, or |  | No | No | No | NO
Washington Gas | Other (please specify) | 49 CFR 192.619 leads us to prescribe tests at minimum 1.5 * 60 = 90 psig. | No | We have been exploring the use of Aeronautical National Pipe Taper (ANPT) threaded fittings. | We have not experienced any issues. | NO
New Mexico Gas Company | ASME B16.33 – Manually Operated Metallic Gas Valves for Use in Gas Piping Systems Up to 175 psi (Sizes NPS ½ Through NPS 2), |  | No | Not at the moment. | NA | NO
PG&E | Other (please specify) | no specific standard- typically 60 psig for 15 seconds | no | no | NA | NO
PECO, an Exelon company | Other (please specify) | We perform pressure tests on our meter assemblies as per customer specs. Customer specs are around the same values (90 to 125 PSI) | No, they haven’t changed. | No, we are not. | The pressure test performed consists of injecting pressure in the meter bar and dunking the pieces into a tank looking for bubbles. We currently don’t use electronic pressure gauges. We use standard pressure gauges. | NO
PECO, an Exelon company | Other (please specify) | We perform pressure tests on our meter assemblies as per customer specs. Customer specs are around the same values (90 to 125 PSI) | No, they haven’t changed. | No, we are not. | The pressure test performed consists of injecting pressure in the meter bar and dunking the pieces into a tank looking for bubbles. We currently don’t use electronic pressure gauges. We use standard pressure gauges. | NO
COMPANY 1 | Other (please specify) | MSA's tested in accordance with pressure testing requirements stipulate in our Operating Procedures Manual. | Not to my knowledge. | Not presently. | Not to my knowledge. | YES
COMPANY 2 | Other (please specify) | Meter set assemblies are built on site | N/A | N/A | N/A | YES
COMPANY 3 | Other (please specify) | Internal testing procedure | No | Yes. example would be bypass meter bar amongst other things but nothing has been formalized. | Supplier only completes traditional leak testing. | YES
COMPANY 4 | Other (please specify) | Prefabricated stands are pressure certified at the manufacturer, locally welded stands are pressure tested 1.5XMAOP, all joints are soap tested upon installation in the field. | Not aware of any changes. | Not at this time. | Not at this time. | YES
COMPANY 5 | Other (please specify) | CSA Z662, identifies ASME B16.33 | N/A | N/A, currently have both BMI fitting based and all welded MSAs. | Traditional leak testing is the current practice. | YES
COMPANY 6 | Other (please specify) | We do not require manufacturers to follow a specific specification to pressure test gas meters | No | No | No | YES
COMPANY 7 | ASME B16.33 – Manually Operated Metallic Gas Valves for Use in Gas Piping Systems Up to 175 psi (Sizes NPS ½ Through NPS 2), | N/A | No | No | No | YES
COMPANY 8 | Other (please specify) | Meter Sets are pressure tested to 1.5 times MAOP for the set, which is 180 PSI. | No | Not at this time. | The MSAs are currently hydrostatically tested. | YES
GAS Summary: Meter Set Assembly
August 2023
AGA Contact: Luis Escobar, Jeff Meyers & Alan Chichester
Note: The survey responses are based on an informal survey and are for general information only. They are not intended to bind any company or state a company's official position. The information represents an unaudited compilation of information and could contain coding or processing errors. Anyone using this document should rely on his or her own independent judgment or, as appropriate, seek the advice of a competent professional. References to work practices, products or vendors do not imply an opinion or endorsement by AGA or a responding company. This publication is confidential and proprietary to AGA. This document is not intended to provide legal advice or opinions. As always, you should consult your legal counsel for advice based on the law and your company’s specific facts and circumstances. The information provide in this summary is for the benefit and internal use of individual AGA members. It should not be discussed among the participants or members nor provided to others.
Copyright & Distribution: Copyright © 2023 American Gas Association. All rights reserved. This work may not be reproduced or transmitted in any form or by any means, electronic or mechanical, including photocopying, recording, or by information storage and retrieval system without permission in writing from the American Gas Association.